Date
SECTION 40 91 13.XX

Project Number
SPECTROMETRIC NITRATE PROCESS MEASUREMENT DEVICES

Project Name
Page 1

PART 1 GENERAL

1.1 DESCRIPTION
A. Section Includes

1. Sensors, cables, and associated equipment for measuring nitrate and total suspended solids (optional) in water and wastewater treatment systems.  Controllers and modules required for a complete monitoring system are specified elsewhere.
B. Scope
1. Furnish, install, calibrate, test, adjust, and place into satisfactory operation spectrometric sensors as shown on the Drawings and specified herein in accordance with the contract documents.

2. The Drawings and Specifications illustrate and specify functional and general construction requirements of spectrometric sensors and do not necessarily show or specify all components, wiring, piping, and accessories required to make a completely integrated system. Provide all components, piping, wiring, accessories, and labor required for a complete workable and integrated system.

C. Coordination:  Coordinate with other suppliers for installation of all items specified herein and required to ensure the complete and proper interfacing of all the components and systems.
1.2 PERFORMANCE REQUIREMENTS

A. Design Requirements

1. Design measurement system for continuous monitoring in situ.  

2. Measurement system shall be a component of a process monitoring system capable of monitoring up to 20 parameters simultaneously on each controller.  Measurement locations shall be networked together in a linear, star, or branched topology with a single 2-wire cable that distributes 12 V power and communications.

3. The measurement system shall be capable of simultaneous display of nitrate and 1 solids parameter from one sensor.

4. The sensor assembly shall be a separate unit from the sensor connection cable and able to be located anywhere in the monitoring network a SensorNet terminal is available.

B. Performance Requirements

1. Operating range

a. Temperature:  32°F to 113°F (0°C to 45°C)
b. Pressure:  less than or equal to 1 bar

c. pH:  4 S.U. to 12 S.U.

d. Flow velocity:  < 3 m/s

2. Measuring range [NitraVis 701 IQ]
a. Nitrate​​
1) Untreated wastewater  
i. 0 mg NO3 / L to 300 mg NO3 / L
ii. 0 mg NO3-N / L to 60 mg NO3-N / L

2) Bioreactor
i. 0 mg NO3 / L to 300 mg NO3 / L
ii. 0 mg NO3-N / L to 60 mg NO3-N / L

3) Treated wastewater
i. 0 mg NO3 / L to 750 mg NO3 / L
ii. 0 mg NO3-N / L to 150 mg NO3-N / L
b. Total Suspended Solids (TSS) [NitraVis 701 (TS)]
1) Untreated wastewater: 0 g TSS / L to 15 g TSS / L
2) Bioreactor:  0 g TSS/ L to 20 g TSS / L
2. Measuring range [NitraVis 705 IQ]

1) Treated wastewater

i. 0 mg NO3 / L to 250 mg NO3 / L
ii. 0 mg NO3-N / L to 50 mg NO3-N / L
2) Total Suspended Solids (TSS) [NitraVis 705 (TS)]

i. Treated wastewater: 0 mg TSS / L to 900 mg TSS / L
3. Resolution [NitraVis 701 IQ]

a. Nitrate​​
1) Untreated wastewater  
i. 0.1 mg NO3 / L

ii. 0.01 mg NO3-N / L

2) Bioreactor

i. 0.1 mg NO3 / L

ii. 0.01 mg NO3-N / L

3) Treated wastewater

i. 0.1 mg NO3 / L

ii. 0.1 mg NO3-N / L
b. Total Suspended Solids (TSS) [NitraVis 701 (TS)]

1) Untreated wastewater: 0.01 g TSS / L

2) Bioreactor:  0.01 g TSS/L 
3. Resolution [NitraVis 705 IQ]
a. Nitrate​​
1) Treated wastewater

i. 0.1 mg NO3 / L

ii. 0.01 mg NO3-N / L
b. Total Suspended Solids (TSS) [NitraVis 705 (TS)]

1) Treated wastewater:  0.1 mg TSS /L

4. Signal averaging:  user selectable to provide a t90 from 10 min. to 60 min. 

1.2 QUALITY ASSURANCE
C. Acceptable Manufacturers:
1. Furnish spectrometric sensors by the named manufacturers. 

2. The named manufacturers have been specified to establish the standard of quality and performance of the equipment to be supplied. 
3. Manufacturer shall be ISO 9001 certified.
1.3 PRODUCT DELIVERY, STORAGE, AND HANDLING
D. Delivery and Acceptance Requirements:  Deliver materials to site in manufacturer’s original, unopened containers and packaging, with labels clearly identifying product name and manufacturer. 

2. Storage and Handling Requirements: 
1. Store and handle materials in accordance with manufacturer’s instructions.
2. Keep materials in manufacturer’s original, unopened containers and packaging until installation.
3. Store materials in clean, dry area indoors.
4. Protect materials during storage, handling, and installation to prevent damage.

5. Temperature range for storage:  15°F to 120°F (-10°C to 50°C)
1.4 SUBMITTALS

E. Product data

1. Sensor operating manual.

2. Mounting bracket / sensor holder installation instructions.

3. Manufacturer’s Certifications:  Submit manufacturer’s certification that materials comply with specified requirements and are suitable for intended application.
4. Warranty documentation:  Submit manufacturer’s standard warranties.
PART 2 PRODUCTS

2.2 GENERAL

F. Measurement principle shall be optical absorption by means of a xenon flash lamp and multi-diode array to measure the transmission of light through wastewater simultaneously from 256 separate wavelengths spanning the ultraviolet and visible light spectrum.  

G. Connect nitrate sensor to field-mounted junction box or expansion modules specified in Section 40 95 00 with sensor connecting cable specified in Section 2.3.A.3.
H. Nitrate measurement system components shall be designed to be part of an analytical process control system with enhanced protection from overvoltage due to lightning and power supply fluctuations according to EN 61326 when installed using manufacturer’s recommended components per manufacturer’s instructions.  
2.3 MANUFACTURER

I. Provide products from the following manufacturer:
1. YSI Incorporated, 1700/1725 Brannum Lane, Yellow Springs, OH  45387.  1-800-765-4974.
2.4 MANUFACTURED UNIT  

J. The spectrometric measurement system consists of the following:

1. Model NitraVis® 70x IQ (TS) spectrometric sensor.

a. The sensor shall use an optical method that measures the absorption spectrum of a sample over a range from ultraviolet to long wave visible light.
b. The sensor shall be factory-calibrated and ready for measurement.
c. The sensor shall have a non-mechanical integrated ultrasonic cleaning system.

d. The sensor shall have a digital output signal.
e. The sensor shall detach from sensor cable allowing for easy replacement or repair.


[image: image1]
2. SACIQ-x,x [SACIQ-x,x SW] sensor connection cable.
a. Capable of transmitting digital communications and low voltage (24V) power

b. Integrated shield.

c. Connections

1) Sensor-side:  Quick fastener (threaded).

2) Controller-side:  tinned conductors


[image: image2]
2.5 MATERIALS
K. Sensor
1. Shaft:  Titanium Grade 2
2. Measurement window:  sapphire

3. Center piece, end cap:  PEEK 
4. Plug head connector housing:  POM 

5. Plug:  ETFE

6. Protective ring:  POM 
7. EMI/RFI conformance

a. EN 61326 Class B

b. FCC Class A

8. Safety

a. Certification: CE,  cETLus
9. Protection rating:  IP68

10. Warranty: 2 yrs.
B. Sensor connection cable
1. Conductors:  Tin-coated stranded copper wire.
2. Coupling ring: Stainless Steel 1.4571 (equivalent to 316Ti)

[image: image3]
3. Ring: POM

Screw: Stainless Steel V4A

[image: image4]
4. O-ring:  NBR
5. Enclosure:  POM
6. Nut:  Stainless Steel 1.4571 (equivalent to 316Ti)

[image: image5]
7. Protection ring:  POM
8. Cable sheath:  PUR
9. Protective cap: PVC


[image: image6]
10. Protection rating:  IP68 (waterproof)
11. Warranty:  12 months

2.6 ACCESSORIES

[image: image7]
L. Handrail swing mounting assembly

1. YSI model 109 281Y BE/ST 170-R Pipe Mounting Stand

2. YSI model 109 272Y Swing Mounting Assembly

3. YSI model 481 073Y Horizontal Chain Mount [horizontal mount]

4. YSI model 109 320Y Single Sensor Holder [vertical mount]
B. Handrail Pipe mounting assembly:   

1. YSI model 2458000Y SMK Quick Release Stainless Steel Handrail Mounting Bracket with 1.5-inch Mounting Adapter
C. Compressed air cleaning system [Options: external air supply; cleaning air box supply]

[image: image8]
1. Model:  Cleaning Air Box


[image: image9]
2. The cleaning system shall use clean, dry, oil free air.

3. Sensor-controlled cleaning cycles.
4. Cleaning set Model SET/AP:  connector and 15 m of tubing.

5. Cleaning pressure: between 30 and 50 psi.
6. Each sensor shall have a dedicated cleaning compressor.


[image: image10]
7. Power supply:  115 VAC.

[image: image11]
PART 3 EXECUTION

3.2 INSTALLATION
M. Immersion sensors:

1. Immerse sensor to a depth sufficient to fill the measuring gap.
2. Protect the probe against the oncoming flow of large objects.

3. Install instrument to prevent air bubbles from gathering on the optical sensing element.
a. Horizontal installation:  Align sensor parallel to flow with measuring gap opening on the side

b. Vertical installation:  Align measuring gap perpendicular to the flow direction.

4. Impact protection

a. Mount shock protectors to absorb inadvertent impacts.

b. Mount sensor so that it cannot knock against a wall or other obstacle.

B. Sensor connection cable

1. Bend radius

a. Permanent bend:  not less than 3.2 in. (80 mm).

b. One-time bend:  not less than 2 in. (50 mm).

3.3 START-UP
A. Install spectrometric sensors in strict accordance with the manufacturer’s instructions and recommendations.

B. Manufacturer’s representative will include a half-day of start-up service by a factory-trained technician, if requested.

1. Contractor will schedule a date and time for start-up.

2. Contractor will require representatives of the following be present during the start-up:
a. General contractor

b. Electrical contractor

c. YSI factory-trained representative

d. Owner’s personnel

e. Engineer

END OF SECTION

Note to specifier:  Select appropriate model and measuring gap (701 models for influent wastewater with 1 mm measuring gap; 705 models for bioreactors and effluent wastewater with 5 mm measuring gap).  Select “TS” model for solids measurement.





Note to specifier:  Specify appropriate length of cable in meters, e.g. SACIQ-1,5 is 1.5 m.   Standard lengths are 1.5 m, 7m, and 15m.  Custom lengths up to 100 m are available.  Select SACIQ-x,x for measurements in water/wastewater applications.  Select SACIQ-x,x SW for measurements in seawater/aquaculture and other highly corrosive environments.





Note to specifier:  specify Titanium, grade 2 for SW model applications.





Note to specifier:  specify Polyamide 6.6 for SW model applications.





Note to specifier:  specify Titanium, grade 2 for SW model applications.





Note to specifier:  specify POM threaded plug for SW model applications.





Note to specifier:  Specify sensor mounting assembly and other accessories as required.





Note to specifier:  Cleaning air box option described.   External air supply option requires a source of air at 45 to 105 psig.  See notes in text boxes for details of external air supply option.





Note to specifier:  For external air supply option specify valve module MIQ/CHV PLUS for use with 2020 XT controller or valve module DIQ/CHV for use with 182 controller.  





Note to specifier:  Not a requirement for external air supply option.





Note to specifier:  Specify 230 VAC if required.  Not a requirement for external air supply option.









